## CID Event Codes
CID | Event Type | Event Description
100 | Medical | A non-specific medical condition exists
101 | Personal Emergency | Emergency Assistance request
102 | Fail to report in | A user has failed to activate a monitoring device
110 | Fire | A non-specific fire alarm condition exists
111 | Smoke | An alarm has been triggered by a smoke detector
112 | Combustion | An alarm has been triggered by a combustion detector
113 | Water Flow | An alarm has been triggered by a water flow detector
114 | Heat | An alarm has been triggered by a heat detector
115 | Pull Station | A pull station has been activated
116 | Duct | An alarm has been triggered by a duct detector
117 | Flame | An alarm has been triggered by a flame detector
118 | Near Alarm | A near-alarm condition has been detected on a fire sensor
120 | Panic | A non-specific hold-up alarm exists
121 | Duress | A duress code has been entered by a user
122 | Silent | A silent hold-up alarm exists
123 | Audible | An audible hold-up alarm exists
124 | Duress Access granted | A duress code has been entered and granted at an entry door
125 | Duress Egress granted | A duress code has been entered and granted at an exit door
126 | Hold-up suspicion print | A user has activated a trigger to indicate a suspicious condition
130 | Burglary | A burglary zone has been violated while armed
131 | Perimeter | A perimeter zone has been violated while armed
132 | Interior | An interior zone has been violated while armed
133 | 24 Hour (Safe) | A 24 hour burglary zone has been violated
134 | Entry/Exit | An Entry/Exit zone has been violated while armed
135 | Day/Night | An trouble by Day / alarm by Night zone has been violated while armed
136 | Outdoor | An outdoor burglary zone has been violated while armed
137 | Tamper | A burglary zone has been tampered with while armed
138 | Near alarm | A burg sensor has detected a condition which will cause it to go into alarm if the condition worsens
139 | Intrusion Verifier | The specified zone has verified that an intrusion has occurred
140 | General Alarm | The specified zone is in an alarm condition
141 | Polling loop open | An open circuit condition has been detected on a polling loop while the system was armed
142 | Polling loop short | A short circuit condition has been detected on a polling loop while the system was armed
143 | Expansion module failure | A general failure condition has been detected on an expansion module while the system was armed
144 | Sensor tamper | A sensor's tamper has been violated (case opened)
145 | Expansion module tamper | An expansion module's tamper has been violated (cabinet opened)
146 | Silent Burglary | A burglary zone has been violated while armed with no audible notification produced
147 | Sensor Supervision Failure | A sensor's supervisory circuit has reported a failure while the system was armed
150 | 24 Hour Non-Burglary | A non-burglary zone has been faulted
151 | Gas detected | The gas detector assigned to the specified zone has reported a fault condition
152 | Refrigeration | The refrigeration detector assigned to the specified zone has reported a fault condition
153 | Loss of heat | The temperature detector assigned to the specified zone has reported a fault condition
154 | Water Leakage | The water leak detector assigned to the specified zone has reported a fault condition
155 | Foil Break | The specified zone which is assigned to foil used as glass break detection has reported a fault condition
156 | Day Trouble | The specified zone which monitors trouble by day has reported a fault condition while disarmed
157 | Low bottled gas level | The gas level detector assigned to the specified zone has reported a fault condition
158 | High temp | The over-temperature detector assigned to the specified zone has reported a fault condition
159 | Low temp | The under-temperature detector assigned to the specified zone has reported a fault condition
161 | Loss of air flow | The air flow detector assigned to the specified zone has reported a fault condition
162 | Carbon Monoxide detected | The carbon monoxide detector assigned to the specified zone has reported a fault condition
163 | Tank level | The tank level detector assigned to the specified zone has reported a fault condition
200 | Fire Supervisory | The supervisory circuit of the specified fire zone has reported a fault condition
201 | Low water pressure | The water pressure sensor assigned to the specified zone has reported a fault condition
202 | Low CO2 | The CO2 pressure sensor assigned to the specified zone has reported a fault condition
203 | Gate valve sensor | The gate valve sensor in the fire sprinkler system assigned to the specified zone has reported a fault condition
204 | Low water level | The water level sensor assigned to the specified zone has reported a fault condition
205 | Pump activated | The pump activity detector assigned to the specified zone has reported an active condition
206 | Pump failure | A pump output monitor assigned to the specified zone has reported a fault condition
300 | System Trouble | A general system trouble condition has been reported by the specified zone
301 | AC Loss | AC power loss has been detected at a control or expansion module while the system was disarmed
302 | Low system battery | A battery has failed a load test while the system was disarmed
303 | RAM Checksum bad | A test of the system's memory has failed
304 | ROM checksum bad | A test of the system's executable memory has failed
305 | System reset | The system has reset and restarted
306 | Panel programming changed | The programmed configuration of the panel has changed
307 | Self-test failure | The system has failed a self-test
308 | System shutdown | The system has been shut down and has stopped functioning
309 | Battery test failure | The system backup battery has failed a load test while the system was disarmed
310 | Ground fault | The panel has detected a ground fault condition
311 | Battery Missing/Dead | The system has detected that the backup battery is either missing or completely discharged.
312 | Power Supply Overcurrent | The system power supply has reported an excessive current draw condition
313 | Engineer Reset | The specified service person has issued a system reset
314 | Radio battery charger failure | The system's primary power supply has failed a supervision test. Radio devices indicate this when the backup battery charging circuit has failed its supervision test
320 | Sounder/Relay | A trouble condition exists in the system's sounder/relay circuit
321 | Bell 1 | A trouble condition exists in the primary bell circuit
322 | Bell 2 | A trouble condition exists in the secondary bell circuit
323 | Alarm relay | A trouble condition exists in the system's alarm relay circuit
324 | Trouble relay | A trouble condition exists in the system's trouble relay circuit
325 | Reversing relay | The specified TELCO reversing relay has reported a trouble condition
326 | Notification Appliance Ckt. # 3 | A trouble condition exists in the bell #3 circuit
327 | Notification Appliance Ckt. #4 | A trouble condition exists in the bell #4 circuit
330 | System Peripheral trouble | A system peripheral device has reported a trouble condition
331 | Polling loop open | An open circuit condition has been detected on a polling loop while the system was disarmed
332 | Polling loop short | A short circuit condition has been detected on a polling loop while the system was disarmed
333 | Expansion module failure | A general failure condition has been detected on an expansion module while the system was disarmed
334 | Repeater failure | A repeater in the system has reported a failure condition while the system was disarmed
335 | Local printer out of paper | The printer attached to the panel has reported an Out Of Paper condition
336 | Local printer failure | The printer attached to the panel has reported a failure condition
337 | Exp. Module Power Loss | An expansion module has detected a DC power loss
338 | Exp. Module Low Battery | An expansion module has detected a low battery condition
339 | Exp. Module Power On / Reset | An expansion module has reset
341 | Exp. Module Tamper | An expansion module has detected its tamper switch has been faulted
342 | Exp. Module AC Loss | An expansion module has detected the loss of AC power
343 | Exp. Module self-test fail | An expansion module has failed a self-test
344 | RF Receiver Jam Detect | An RF receiver has detected the presence of a jamming signal which prevents it from receiving normal signalsfrom the system RF devices
350 | Communication Path Failure | The system has experienced difficulties communicating with the central station
351 | Telco 1 fault | The system has detected a fault on the primary dial-up line
352 | Telco 2 fault | The system has detected a fault on the secondary dial-up line
353 | Long Range Radio xmitter fault | A fault has been detected in the long range radio subsystem
354 | Failure to communicate event | The system was unable to communicate an event to the central station
355 | Loss of Radio ECP supervision | The radio has not reported in its designated supervision interval
356 | Loss of central polling | The radio has detected a loss in the polling signal from it's associated receiver
357 | Long Range Radio VSWR problem | The Long Range Radio has reported a transmitter/antenna problem
358 | Periodic Comm Test Fail /Restore | A periodic Communication path test has failed
370 | Protection loop | The specified protection loop has reported a trouble condition
371 | Protection loop open | The specified protection loop has reported an open-loop trouble condition
372 | Protection loop short | The specified protection loop has reported a shorted-loop trouble condition
373 | Fire trouble | A fire sensor has detected a trouble condition on the specified zone while the system was disarmed
374 | Exit error alarm (zone) | An exit error condition has been reported for the specified alarm zone
375 | Panic zone trouble | The system has detected a trouble condition on the panic zone
376 | Hold-up zone trouble | The system has detected a trouble condition on the hold-up zone
377 | Swinger Trouble | A fault has occurred on a zone that has been shut down due to excessive alarms
378 | Cross-zone Trouble | The specified zone in a cross-zone configuration has faulted without a fault on its corresponding cross-zone ina specific time period
380 | Sensor trouble | The specified sensor has reported a trouble condition
381 | Loss of supervision - RF | The specified zone has failed to report in during its designated supervision period
382 | Loss of supervision - RPM | An Remote Polled Module assigned to the specified zone has failed supervision
383 | Sensor tamper | The tamper switch on the specified sensor has been faulted
384 | RF low battery | The specified battery powered RF zone has reported a low battery condition
385 | Smoke detector Hi sensitivity | A smoke detector's sensitivity level has drifted to the upper limit
386 | Smoke detector Low sensitivity | A smoke detector's sensitivity level has drifted to the lower limit
387 | Intrusion detector Hi sensitivity | An intrusion detector's sensitivity level has drifted to the upper limit
388 | Intrusion detector Low sensitivity | An intrusion detector's sensitivity level has drifted to the lower limit
389 | Sensor self-test failure | The specified sensor has failed a self-test
391 | Sensor Watch trouble | A motion sensor has not been triggered within a pre-defined time interval
392 | Drift Compensation Error | A smoke detector cannot automatically adjust its sensitivity
393 | Maintenance Alert | The specified zone requires maintenance
394 | CO Detector needs replacement | The specified Carbon Monoxide detector has reached end-of-life
400 | Open/Close | The specified user has disarmed/armed the system
401 | O/C by user | The specified user has disarmed/armed the system
402 | Group O/C | A group of zones has been armed or disarmed
403 | Automatic O/C | A partition has been automatically armed or disarmed
404 | Late to O/C (Note: use 453 or 454 instead) | Late to Open or Close
405 | Deferred O/C (Obsolete- do not use ) | Deferred Open or Close
406 | Cancel | The specified user has cancelled the previously reported alarm condition
407 | Remote arm/disarm | The specified user has armed or disarmed the system from off-premises
408 | Quick arm | The specified user has quick-armed the system
409 | Keyswitch O/C | The specified user has armed or disarmed the system using a keyswitch
411 | Callback request made | A remote site (central station) has requested the panel call it back
412 | Successful download/access | The configuration data of the system has been successfully downloaded
413 | Unsuccessful access | A number of failed attempts have been made to remotely access the system
414 | System shutdown command received | A central station has sent a system shutdown command to the panel
415 | Dialer shutdown command received | A central station has sent a dialer shutdown command to the panel
416 | Successful Upload | The configuration data of the system has been successfully uploaded
421 | Access denied | The access control system has denied access to the specified user
422 | Access report by user
423 | Forced Access | The specified access control door has been forced open
424 | Egress Denied | The access control system has denied egress to the specified user
425 | Egress Granted | The access control system has granted egress for the specified user
426 | Access Door propped open | The specified access control door has been held open
427 | Access point Door Status Monitor trouble | The specified Access Point's Door Status Monitor has reported a trouble condition to the panel
428 | Access point Request To Exit trouble | The specified Access Point's Request To Exit zone has reported a trouble condition to the panel
429 | Access program mode entry | The access control system has been put into program mode
430 | Access program mode exit | The access control system has exited program mode
431 | Access threat level change | The access control system's threat level has been changed
432 | Access relay/trigger fail | The specified access control output device has failed to operate properly
433 | Access RTE shunt | The specified Request To Exit zone has been shunted and will no longer report activity
434 | Access DSM shunt | The specified Door Status Monitor zone has been shunted and will no longer report activity
435 | Second Person Access | A second person has accessed an access point conforming to Two-Man-Rule requirements
436 | Irregular Access
441 | Armed STAY | The specified user has armed the system in STAY mode
442 | Keyswitch Armed STAY | The specified user has armed the system in STAY mode using a keyswitch
443 | Armed with System Trouble Override | The specified user has armed the system while overriding a trouble condition
450 | Exception O/C | The system has been armed or disarmed outside of the configured time window
451 | Early O/C | The system has been disarmed/armed by the specified user before the configured time window has started
452 | Late O/C | The system has been disarmed/armed by the specified user after the configured time window has ended
453 | Failed to Open | The system has failed to have been disarmed during the designated time window
454 | Failed to Close | The system has failed to be armed during the designated time window
455 | Auto-arm Failed | The system has failed to automatically arm itself at the designated time
456 | Partial Arm | The system has been only partially armed by the specified user
457 | Exit Error (user) | The specified user has made an error exiting the premises after arming the system
458 | User on Premises | A user has disarmed the system after an alarm has occurred
459 | Recent Close | The system had been armed within the last xx minutes
461 | Wrong Code Entry
462 | Legal Code Entry
463 | Re-arm after Alarm
464 | Auto-arm Time Extended | A user has successfully requested that the system delay automatically arming
465 | Panic Alarm Reset | The specified panic zone has been reset
466 | Service On/Off Premises | A service person has entered or left the premises
501 | Access reader disable | The credential reader on the specified access point has been disabled
520 | Sounder/Relay Disable | The specified sounder or relay has been disabled
521 | Bell 1 disable | The specified output for Bell 1 has been disabled
522 | Bell 2 disable | The specified output for Bell 2 has been disabled
523 | Alarm relay disable | The specified alarm relay has been disabled
524 | Trouble relay disable | The specified trouble relay has been disabled
525 | Reversing relay disable | The specified reversing relay has been disabled
526 | Notification Appliance Ckt. # 3 disable | The specified output for Bell 3 has been disabled
527 | Notification Appliance Ckt. # 4 disable | The specified output for Bell 4 has been disabled
531 | Module Added | The specified access control module has been added to the system
532 | Module Removed | The specified access control module has been removed from the system
551 | Dialer disabled | The specified dialer has been disabled
552 | Radio transmitter disabled | The specified radio transmitter has been disabled
553 | Remote Upload/Download disabled | Remote configuration has been enabled
570 | Zone/Sensor bypass | The specified zone or sensor has been bypassed
571 | Fire bypass | The specified fire zone has been bypassed
572 | 24 Hour zone bypass | The specified 24 hour zone has been bypassed
573 | Burg. Bypass | The specified burglary zone has been bypassed
574 | Group bypass | A group of zones has been bypassed
575 | Swinger bypass | The specified zone which has reported an excessive number of faults/restores in a short period of time has been bypassed
576 | Access zone shunt | The specified zone in the access control system has been shunted and will no longer report activity
577 | Access point bypass | The specified access point in the access control system has been bypassed and will allow the door to open(unsecured)
578 | Vault Bypass | The specified vault zone has been bypassed
579 | Vent Zone Bypass | The specified vent zone has been bypassed and will no longer report any activity
601 | Manual trigger test report | A test report has been triggered manually
602 | Periodic test report | A periodic test report has been triggered
603 | Periodic RF transmission | A periodic RF path test report has been triggered
604 | Fire test | The specified user has initiated a test of the fire alarm zones
605 | Status report to follow
606 | Listen-in to follow | The system is about to activate a 2-way audio session
607 | Walk test mode | The specified user has placed the system into the walk-test mode for testing purposes
608 | Periodic test - System Trouble Present | A periodic test has been triggered but the fire system has a trouble condition present
609 | Video Xmitter active | A video look-in session is about to begin
611 | Point tested OK | The specified point tested successfully
612 | Point not tested | The specified point has not been tested
613 | Intrusion Zone Walk Tested | The specified intrusion zone has been successfully walk-tested
614 | Fire Zone Walk Tested | The specified fire zone has been successfully walk-tested
615 | Panic Zone Walk Tested | The specified panic zone has been successfully walk-tested
616 | Service Request | A request has been made for system servicing
621 | Event Log reset | The event log has been reset and all stored events have been discarded
622 | Event Log 50% full | The event log is 50% full
623 | Event Log 90% full | The event log is 90% full
624 | Event Log overflow | The event log has overflowed and events have been lost
625 | Time/Date reset | The time and date have been reset to a new value by the specified user
626 | Time/Date inaccurate | The system time and date is known to be in error
627 | Program mode entry | The system has been placed into program mode
628 | Program mode exit | The system has exited program mode
629 | 32 Hour Event log marker | In the last 31.9 hours (1 and 1/3 days), nothing has been posted to the event log. There is nothing new toread. Does not send to central station and only occurs in the Vista-20/SE and FA sister products.
630 | Schedule change | The specified fire/burglary schedule has been changed
631 | Exception schedule change | The time schedule for event reporting by exception has been changed
632 | Access schedule change | The specified access control schedule has been changed
641 | Senior Watch Trouble | A person has not activated a motion sensor in a specified period
642 | Latch-key Supervision | A child has disarmed the system (after school)
651 | Reserved for Ademco Use
652 | Reserved for Ademco Use
653 | Reserved for Ademco Use
654 | System Inactivity | System has not been operated for x days
655 | User Code X modified by Installer | The Installer has modified the specified User's code
703 | Auxiliary #3
704 | Installer Test
750 | User Assigned CID Message
751 | User Assigned CID Message
752 | User Assigned CID Message
753 | User Assigned CID Message
754 | User Assigned CID Message
755 | User Assigned CID Message
756 | User Assigned CID Message
757 | User Assigned CID Message
758 | User Assigned CID Message
759 | User Assigned CID Message
760 | User Assigned CID Message
761 | User Assigned CID Message
762 | User Assigned CID Message
763 | User Assigned CID Message
764 | User Assigned CID Message
765 | User Assigned CID Message
766 | User Assigned CID Message
767 | User Assigned CID Message
768 | User Assigned CID Message
769 | User Assigned CID Message
770 | User Assigned CID Message
771 | User Assigned CID Message
772 | User Assigned CID Message
773 | User Assigned CID Message
774 | User Assigned CID Message
775 | User Assigned CID Message
776 | User Assigned CID Message
777 | User Assigned CID Message
778 | User Assigned CID Message
779 | User Assigned CID Message
780 | User Assigned CID Message
781 | User Assigned CID Message
782 | User Assigned CID Message
783 | User Assigned CID Message
784 | User Assigned CID Message
785 | User Assigned CID Message
786 | User Assigned CID Message
787 | User Assigned CID Message
788 | User Assigned CID Message
789 | User Assigned CID Message
796 | Unable to output signal (Derived Channel
798 | STU Controller down (Derived Channel)
900 | Download Abort | The specified Downloader ID has aborted a download sequence in progress
901 | Download Start/End | Downloader has started or ended a download sequence to the panel
902 | Download Interrupted | A download sequence has been interrupted
910 | Auto-close with Bypass | An auto-close sequence has been started and the specified zone has been bypassed
911 | Bypass Closing
912 | Fire Alarm Silence | The fire alarm has been silenced
913 | Supervisory Point test Start/End | A fire supervisory device has been tested
914 | Hold-up test Start/End | The specified user has started or ended a hold-up test
915 | Burg. Test Print Start/End | The printed progress of a burglary test has been started or ended
916 | Supervisory Test Print Start/End | The printed progress of a supervisory test has been started or ended
917 | Burg. Diagnostics Start/End | A burglary system diagnostic test has been started or ended
918 | Fire Diagnostics Start/End | A fire system diagnostic test has been started or ended
919 | Untyped diagnostics
920 | Trouble Closing (closed with burg. Durin exit)
921 | Access Denied Code Unknown | Access has been denied because the system did not recognize the supplied access code as valid
922 | Supervisory Point Alarm | The specified supervisory point has reported an alarm condition
923 | Supervisory Point Bypass | The specified supervisory point has been bypassed
924 | Supervisory Point Trouble | The specified supervisory point has reported a trouble condition
925 | Hold-up Point Bypass | The specified hold-up point has been bypassed
926 | AC Failure for 4 hours | There has been a loss of AC power for at least four hours
927 | Output Trouble | The specified output has reported a trouble condition
928 | User code for event | This message contains the ID of the user who triggered the previous event
929 | Log-off | The specified user has logged-off of the system
954 | Communication Failure | Comm fail to the primary (zone 951) or secondary (zone 952) 7810iR-ent in private LAN mode
999 | 1 and 1/3 Day No Read Log | In the last 31.9 hours (1 and 1/3 days), nothing has been posted to the event log. There is nothing new toread. Does not send to central station and only occurs in the Vista-20/SE and FA sister products.

## SIA Event Codes
Data Code | Short Description | Long Description | Address Field
AA | Alarm – Panel Substitution | An attempt to substitute an alternate alarm panel for a secure panel has been made | Condition number
AB | Abort | An event message was not sent due to User action | Zone or point
AN | Analog Restoral | An analog fire sensor has been restored to normal operation | Zone or point
AR | AC Restoral | AC power has been restored | Unused
AS | Analog Service | An analog fire sensor needs to be cleaned or calibrated | Zone or point
AT | AC Trouble | AC power has been failed | Unused
BA | Burglary Alarm | Burglary zone has been violated while armed | Zone or point
BB | Burglary Bypass | Burglary zone has been bypassed | Zone or point
BC | Burglary Cancel | Alarm has been cancelled by authorized user | User number
BD | Swinger Trouble | A non-fire zone has been violated after a Swinger Shutdown on the zone | Zone or point
BE | Swinger Trouble Restore | A non-fire zone restores to normal from a Swinger Trouble state | Zone or point
BG | Unverified Event - Burglary | A point assigned to a Cross Point group has gone into alarm but the Cross Point remained normal | Zone or point
BH | Burglary Alarm Restore | Alarm condition eliminated | Zone or point
BJ | Burglary Trouble Restore | Trouble condition eliminated | Zone or point
BM | Burglary Alarm - Cross Point | Burglary alarm w/cross point also in alarm - alarm verified | Zone or point
BR | Burglary Restoral | Alarm/trouble condition has been eliminated | Zone or point
BS | Burglary Supervisory | Unsafe intrusion detection system condition | Zone or point
BT | Burglary Trouble | Burglary zone disabled by fault | Zone or point
BU | Burglary Unbypass | Zone bypass has been removed | Zone or point
BV | Burglary Verified | A burglary alarm has occurred and been verified within programmed conditions. (zone or point not sent) | Area number
BX | Burglary Test | Burglary zone activated during testing | Zone or point
BZ | Missing Supervision | A non-fire Supervisory point has gone missing | Zone or point
CA | Automatic Closing | System armed automatically | Area number
CD | Closing Delinquent | The system has not been armed for a programmed amount of time | Area number
CE | Closing Extend | Extend closing time | User number
CF | Forced Closing | System armed, some zones not ready | User number
CG | Close Area | System has been partially armed | Area number
CI | Fail to Close | An area has not been armed at the end of the closing window | Area number
CJ | Late Close | An area was armed after the closing window | User number
CK | Early Close | An area was armed before the closing window | User number
CL | Closing Report | System armed, normal | User number
CM | Missing Alarm - Recent Closing | A point has gone missing within 2 minutes of closing | Zone or point
CO | Command Sent | A command has been sent to an expansion/peripheral device | Condition number
CP | Automatic Closing | System armed automatically | User number
CQ | Remote Closing | The system was armed from a remote location | User number
CR | Recent Closing | An alarm occurred within five minutes after the system was closed | User number
CS | Closing Keyswitch | Account has been armed by keyswitch | Zone or point
CT | Late to Open | System was not disarmed on time | Area number
CW | Was Force Armed | Header for a force armed session, forced point msgs may follow | Area number
CX | Custom Function Executed | The panel has executed a preprogrammed set of instructions | Custom Functionnumber
CZ | Point Closing | A point, as opposed to a whole area or account, has closed | Zone or point
DA | Card Assigned | An access ID has been added to the controller | User number
DB | Card Deleted | An access ID has been deleted from the controller | User number
DC | Access Closed | Access to all users prohibited | Door number
DD | Access Denied | Access denied, unknown code | Door number
DE | Request to Enter | An access point was opened via a Request to Enter device | Door number
DF | Door Forced | Door opened without access request | Door number
DG | Access Granted | Door access granted | Door number
DH | Door Left Open - Restoral | An access point in a Door Left Open state has restored | Door number
DI | Access Denied – Passback | Access denied because credential has not exited area before attempting to re-enter same area | Door number
DJ | Door Forced - Trouble | An access point has been forced open in an unarmed area | Door number
DK | Access Lockout | Access denied, known code | Door number
DL | Door Left Open - Alarm | An open access point when open time expired in an armed area | Door number
DM | Door Left Open - Trouble | An open access point when open time expired in an unarmed area | Door number
DN | Door Left Open (non-alarm, non-trouble) | An access point was open when the door cycle time expired | Door number
DO | Access Open | Access to authorized users allowed | Door number
DP | Access Denied - Unauthorized Time | An access request was denied because the request is occurring outside the user’s authorized time window(s) | Door number
DQ | Access Denied Unauthorized Arming State | An access request was denied because the user was not authorized in this area when the area was armed | Door number
DR | Door Restoral | Access alarm/trouble condition eliminated | Door number
DS | Door Station | Identifies door for next report | Door number
DT | Access Trouble | Access system trouble | Unused
DU | Dealer ID | Dealer ID number | Dealer ID
DV | Access Denied Unauthorized Entry Level | An access request was denied because the user is not authorized in this area | Door number
DW | Access Denied - Interlock | An access request was denied because the doors associated Interlock point is open | Door number
DX | Request to Exit | An access point was opened via a Request to Exit device | Door number
DY | Door Locked | The door’s lock has been engaged | Door number
DZ | Access Denied - Door Secured | An access request was denied because the door has been placed in an Access Closed state | Door number
EA | Exit Alarm | An exit zone remained violated at the end of the exit delay period | Zone or point
EE | Exit Error | An exit zone remained violated at the end of the exit delay period | User number
EJ | Expansion Tamper Restore | Expansion device tamper restoral | Expansion devicenumber
EM | Expansion Device Missing | Expansion device missing | Expansion devicenumber
EN | Expansion Missing Restore | Expansion device communications re-established | Expansion devicenumber
ER | Expansion Restoral | Expansion device trouble eliminated | Expander number
ES | Expansion Device Tamper | Expansion device enclosure tamper | Expansion devicenumber
ET | Expansion Trouble | Expansion device trouble | Expander number
EX | External Device Condition | A specific reportable condition is detected on an external device | Device number
EZ | Missing Alarm - Exit Error | A point remained missing at the end of the exit delay period | Point number
FA | Fire Alarm | Fire condition detected | Zone or point
FB | Fire Bypass | Zone has been bypassed | Zone or point
FC | Fire Cancel | A Fire Alarm has been cancelled by an authorized person | Zone or point
FG | Unverified Event – Fire | A point assigned to a Cross Point group has gone into alarm but the Cross Point remained normal | Zone or point
FH | Fire Alarm Restore | Alarm condition eliminated | Zone or point
FI | Fire Test Begin | The transmitter area's fire test has begun | Area number
FJ | Fire Trouble Restore | Trouble condition eliminated | Zone or point
FK | Fire Test End | The transmitter area's fire test has ended | Area number
FL | Fire Alarm Silenced | The fire panel’s sounder was silenced by command | Zone or point
FM | Fire Alarm - Cross Point | Fire Alarm with Cross Point also in alarm verifying the Fire Alarm | Point number
FQ | Fire Supervisory Trouble Restore | A fire supervisory zone that was in trouble condition has now restored to normal | Zone or point
FR | Fire Restoral | Alarm/trouble condition has been eliminated | Zone or point
FS | Fire Supervisory | Unsafe fire detection system condition | Zone or point
FT | Fire Trouble | Zone disabled by fault | Zone or point
FU | Fire Unbypass | Bypass has been removed | Zone or point
FV | Fire Supervision Restore | A fire supervision zone that was in alarm has restored to normal | Zone or point
FW | Fire Supervisory Trouble | A fire supervisory zone is now in a trouble condition | Zone or point
FX | Fire Test | Fire zone activated during test | Zone or point
FY | Missing Fire Trouble | A fire point is now logically missing | Zone or point
FZ | Missing Fire Supervision | A Fire Supervisory point has gone missing | Zone or point
GA | Gas Alarm | Gas alarm condition detected | Zone or point
GB | Gas Bypass | Zone has been bypassed | Zone or point
GH | Gas Alarm Restore | Alarm condition eliminated | Zone or point
GJ | Gas Trouble Restore | Trouble condition eliminated | Zone or point
GR | Gas Restoral | Alarm/trouble condition has been eliminated | Zone or point
GS | Gas Supervisory | Unsafe gas detection system condition | Zone or point
GT | Gas Trouble | Zone disabled by fault | Zone or point
GU | Gas Unbypass | Bypass has been removed | Zone or point
GX | Gas Test | Zone activated during test | Zone or point
HA | Holdup Alarm | Silent alarm, user under duress | Zone or point
HB | Holdup Bypass | Zone has been bypassed | Zone or point
HH | Holdup Alarm Restore | Alarm condition eliminated | Zone or point
HJ | Holdup Trouble Restore | Trouble condition eliminated | Zone or point
HR | Holdup Restoral | Alarm/trouble condition has been eliminated | Zone or point
HS | Holdup Supervisory | Unsafe holdup system condition | Zone or point
HT | Holdup Trouble | Zone disabled by fault | Zone or point
HU | Holdup Unbypass | Bypass has been removed | Zone or point
IA | Equipment Failure Condition | A specific, reportable condition is detected on a device | Point number
IR | Equipment Fail - Restoral | The equipment condition has been restored to normal | Point number
JA | User Code Tamper | Too many unsuccessful attempts have been made to enter a user ID | Area number
JD | Date Changed | The date was changed in the transmitter/receiver | User number
JH | Holiday Changed | The transmitter's holiday schedule has been changed | User number
JK | Latchkey Alert | A designated user passcode has not been entered during a scheduled time window | User number
JL | Log Threshold | The transmitter's log memory has reached its threshold level | Unused
JO | Log Overflow | The transmitter's log memory has overflowed | Unused
JP | User On Premises | A designated user passcode has been used to gain access to the premises. | User number
JR | Schedule Executed | An automatic scheduled event was executed | Area number
JS | Schedule Changed | An automatic schedule was changed | User number
JT | Time Changed | The time was changed in the transmitter/receiver | User number
JV | User Code Changed | A user's code has been changed | User number
JX | User Code Deleted | A user's code has been removed | User number
JY | User Code Added | A user’s code has been added | User number
JZ | User Level Set | A user’s authority level has been set | User number
KA | Heat Alarm | High temperature detected on premise | Zone or point
KB | Heat Bypass | Zone has been bypassed | Zone or point
KH | Heat Alarm Restore | Alarm condition eliminated | Zone or point
KJ | Heat Trouble Restore | Trouble condition eliminated | Zone or point
KR | Heat Restoral | Alarm/trouble condition has been eliminated | Zone or point
KS | Heat Supervisory | Unsafe heat detection system condition | Zone or point
KT | Heat Trouble | Zone disabled by fault | Zone or point
KU | Heat Unbypass | Bypass has been removed | Zone or point
LB | Local Program | Begin local programming | Unused
LD | Local Program Denied | Access code incorrect | Unused
LE | Listen-in Ended | The listen-in session has been terminated | Unused
LF | Listen-in Begin | The listen-in session with the RECEIVER has begun | Unused
LR | Phone Line Restoral | Phone line restored to service | Line number
LS | Local Program Success | Local programming successful | Unused
LT | Phone Line Trouble | Phone line trouble report | Line number
LU | Local Program Fail | Local programming unsuccessful | Unused
LX | Local Programming Ended | A local programming session has been terminated | Unused
MA | Medical Alarm | Emergency assistance request | Zone or point
MB | Medical Bypass | Zone has been bypassed | Zone or point
MH | Medical Alarm Restore | Alarm condition eliminated | Zone or point
MI | Message | A canned message is being sent | Message number
MJ | Medical Trouble Restore | Trouble condition eliminated | Zone or point
MR | Medical Restoral | Alarm/trouble condition has been eliminated | Zone or point
MS | Medical Supervisory | Unsafe system condition exists | Zone or point
MT | Medical Trouble | Zone disabled by fault | Zone or point
MU | Medical Unbypass | Bypass has been removed | Zone or point
NA | No Activity | There has been no zone activity for a programmed amount of time | Zone number
NC | Network Condition | A communications network has a specific reportable condition | Network number
NF | Forced Perimeter Arm | Some zones/points not ready | Area number
NL | Perimeter Armed | An area has been perimeter armed | Area number
NM | Perimeter Armed, User Defined | A user defined area has been perimeter armed | Area number
NR | Network Restoral | A communications network has returned to normal operation | Network number
NS | Activity Resumed | A zone has detected activity after an alert | Zone number
NT | Network Failure | A communications network has failed | Network number
OA | Automatic Opening | System has disarmed automatically | Area number
OC | Cancel Report | Untyped zone cancel | User number
OG | Open Area | System has been partially disarmed | Area number
OH | Early to Open from Alarm | An area in alarm was disarmed before the opening window | User number
OI | Fail to Open | An area has not been armed at the end of the opening window | Area number
OJ | Late Open | An area was disarmed after the opening window | User number
OK | Early Open | An area was disarmed before the opening window | User number
OL | Late to Open from Alarm | An area in alarm was disarmed after the opening window | User number
OP | Opening Report | Account was disarmed | User number
OQ | Remote Opening | The system was disarmed from a remote location | User number
OR | Disarm From Alarm | Account in alarm was reset/disarmed | User number
OS | Opening Keyswitch | Account has been disarmed by keyswitch | Zone or point
OT | Late To Close | System was not armed on time | User number
OU | Output State – Trouble | An output on a peripheral device or NAC is not functioning | Output number
OV | Output State – Restore | An output on a peripheral device or NAC is back to normal operation | Output number
OZ | Point Opening | A point, rather than a full area or account, disarmed | Zone or point
PA | Panic Alarm | Emergency assistance request, manually activated | Zone or point
PB | Panic Bypass | Panic zone has been bypassed | Zone or point
PH | Panic Alarm Restore | Alarm condition eliminated | Zone or point
PJ | Panic Trouble Restore | Trouble condition eliminated | Zone or point
PR | Panic Restoral | Alarm/trouble condition has been eliminated | Zone or point
PS | Panic Supervisory | Unsafe system condition exists | Zone or point
PT | Panic Trouble | Zone disabled by fault | Zone or point
PU | Panic Unbypass | Panic zone bypass has been removed | Zone or point
QA | Emergency Alarm | Emergency assistance request | Zone or point
QB | Emergency Bypass | Zone has been bypassed | Zone or point
QH | Emergency Alarm Restore | Alarm condition has been eliminated | Zone or point
QJ | Emergency Trouble Restore | Trouble condition has been eliminated | Zone or point
QR | Emergency Restoral | Alarm/trouble condition has been eliminated | Zone or point
QS | Emergency Supervisory | Unsafe system condition exists | Zone or point
QT | Emergency Trouble | Zone disabled by fault | Zone or point
QU | Emergency Unbypass | Bypass has been removed | Zone or point
RA | Remote Programmer Call Failed | Transmitter failed to communicate with the remote programmer | Unused
RB | Remote Program Begin | Remote programming session initiated | Unused
RC | Relay Close | A relay has energized | Relay number
RD | Remote Program Denied | Access passcode incorrect | Unused
RN | Remote Reset | A TRANSMITTER was reset via a remote programmer | Unused
RO | Relay Open | A relay has de-energized | Relay number
RP | Automatic Test | Automatic communication test report | Unused
RR | Power Up | System lost power, is now restored | Unused
RS | Remote Program Success | Remote programming successful | Unused
RT | Data Lost | Dialer data lost, transmission error | Line number
RU | Remote Program Fail | Remote programming unsuccessful | Unused
RX | Manual Test | Manual communication test report | User number
RY | Test Off Normal | Test signal(s) indicates abnormal condition(s) exist | Zone or point
SA | Sprinkler Alarm | Sprinkler flow condition exists | Zone or point
SB | Sprinkler Bypass | Sprinkler zone has been bypassed | Zone or point
SC | Change of State | An expansion/peripheral device is reporting a new condition or state change | Condition number
SH | Sprinkler Alarm Restore | Alarm condition eliminated | Zone or point
SJ | Sprinkler Trouble Restore | Trouble condition eliminated | Zone or point
SR | Sprinkler Restoral | Alarm/trouble condition has been eliminated | Zone or point
SS | Sprinkler Supervisory | Unsafe sprinkler system condition | Zone or point
ST | Sprinkler Trouble | Zone disabled by fault | Zone or point
SU | Sprinkler Unbypass | Sprinkler zone bypass has been removed | Zone or point
TA | Tamper Alarm | Alarm equipment enclosure opened | Zone or point
TB | Tamper Bypass | Tamper detection has been bypassed | Zone or point
TC | All Points Tested | All point tested | Unused
TE | Test End | Communicator restored to operation | Unused
TH | Tamper Alarm Restore | An Expansion Device’s tamper switch restores to normal from an Alarm state | Unused
TJ | Tamper Trouble Restore | An Expansion Device’s tamper switch restores to normal from a Trouble state | Unused
TP | Walk Test Point | This point was tested during a Walk Test | Point number
TR | Tamper Restoral | Alarm equipment enclosure has been closed | Zone or point
TS | Test Start | Communicator taken out of operation | Unused
TT | Tamper Trouble | Equipment enclosure opened in disarmed state | Zone or point
TU | Tamper Unbypass | Tamper detection bypass has been removed | Zone or point
TW | Area Watch Start | Area watch feature has been activated | Unused
TX | Test Report | An unspecified (manual or automatic) communicator test | Unused
TZ | Area Watch End | Area watch feature has been deactivated | Unused
UA | Untyped Zone Alarm | Alarm condition from zone of unknown type | Zone or point
UB | Untyped Zone Bypass | Zone of unknown type has been bypassed | Zone or point
UG | Unverified Event – Untyped | A point assigned to a Cross Point group has gone into alarm but the Cross Point remained normal | Zone or point
UH | Untyped Alarm Restore | Alarm condition eliminated | Zone or point
UJ | Untyped Trouble Restore | Trouble condition eliminated | Zone or point
UR | Untyped Zone Restoral | Alarm/trouble condition eliminated from zone of unknown type | Zone or point
US | Untyped Zone Supervisory | Unsafe condition from zone of unknown type | Zone or point
UT | Untyped Zone Trouble | Trouble condition from zone of unknown type | Zone or point
UU | Untyped Zone Unbypass | Bypass on zone of unknown type has been removed | Zone or point
UX | Undefined | An undefined alarm condition has occurred | Unused
UY | Untyped Missing Trouble | A point or device which was not armed is now logically missing | Zone or point
UZ | Untyped Missing Alarm | A point or device which was armed is now logically missing | Zone or point
VI | Printer Paper In | TRANSMITTER or RECEIVER paper in | Printer number
VO | Printer Paper Out | TRANSMITTER or RECEIVER paper out | Printer number
VR | Printer Restore | TRANSMITTER or RECEIVER trouble restored | Printer number
VT | Printer Trouble | TRANSMITTER or RECEIVER trouble | Printer number
VX | Printer Test | TRANSMITTER or RECEIVER test | Printer number
VY | Printer Online | RECEIVER’S printer is now online | Unused
VZ | Printer Offline | RECEIVER’S printer is now offline | Unused
WA | Water Alarm | Water detected at protected premises | Zone or point
WB | Water Bypass | Water detection has been bypassed | Zone or point
WH | Water Alarm Restore | Water alarm condition eliminated | Zone or point
WJ | Water Trouble Restore | Water trouble condition eliminated | Zone or point
WR | Water Restoral | Water alarm/trouble condition has been eliminated | Zone or point
WS | Water Supervisory | Water unsafe water detection system condition | Zone or point
WT | Water Trouble | Water zone disabled by fault | Zone or point
WU | Water Unbypass | Water detection bypass has been removed | Zone or point
XA | Extra Account Report | CS RECEIVER has received an event from a non-existent account | Unused
XE | Extra Point | Panel has sensed an extra point not specified for this site | Point number
XF | Extra RF Point | Panel has sensed an extra RF point not specified for this site | Point number
XH | RF Interference Restoral | A radio device is no longer detecting RF Interference | Receiver number
XI | Sensor Reset | A user has reset a sensor | Zone or point
XJ | RF Receiver Tamper Restoral | A Tamper condition at a premises RF Receiver has been restored | Receiver number
XL | Low Received Signal Strength | The RF signal strength of a reported event is below minimum level | Receiver number
XM | Missing Alarm - Cross Point | Missing Alarm verified by Cross Point in Alarm (or missing) | Zone or point
XQ | RF Interference | A radio device is detecting RF Interference | Receiver number
XR | Transmitter Battery Restoral | Low battery has been corrected | Zone or point
XS | RF Receiver Tamper | A Tamper condition at a premises receiver is detected | Receiver number
XT | Transmitter Battery Trouble | Low battery in wireless transmitter | Zone or point
XW | Forced Point | A point was forced out of the system at arm time | Zone or point
XX | Fail to Test | A specific test from a panel was not received | Unused
YA | Bell Fault | A trouble condition has been detected on a Local Bell, Siren, or Annunciator | Unused
YB | Busy Seconds | Percent of time receiver's line card is on-line | Line card number
YC | Communications Fail | RECEIVER and TRANSMITTER | Unused
YD | Receiver Line Card Trouble | A line card identified by the passed address is in trouble | Line card number
YE | Receiver Line Card Restored | A line card identified by the passed address is restored | Line card number
YF | Parameter Checksum Fail | System data corrupted | Unused
YG | Parameter Changed | A TRANSMITTER’S parameters have been changed | Unused
YH | Bell Restored | A trouble condition has been restored on a Local Bell, Siren, or Annunciator | Unused
YI | Overcurrent Trouble | An Expansion Device has detected an overcurrent condition | Unused
YJ | Overcurrent Restore | An Expansion Device has restored from an overcurrent condition | Unused
YK | Communications Restoral | TRANSMITTER has resumed communication with a RECEIVER | Unused
YM | System Battery Missing | TRANSMITTER/RECEIVER battery is missing | Unused
YN | Invalid Report | TRANSMITTER has sent a packet with invalid data | Unused
YO | Unknown Message | An unknown message was received from automation or the printer | Unused
YP | Power Supply Trouble | TRANSMITTER/RECEIVER has a problem with the power supply | Unused
YQ | Power Supply Restored | TRANSMITTER’S/RECEIVER’S power supply has been restored | Unused
YR | System Battery Restoral | Low battery has been corrected | Unused
YS | Communications Trouble | RECEIVER and TRANSMITTER | Unused
YT | System Battery Trouble | Low battery in control/communicator | Unused
YU | Diagnostic Error | An expansion/peripheral device is reporting a diagnostic error | Condition number
YW | Watchdog Reset | The TRANSMITTER created an internal reset | Unused
YX | Service Required | A TRANSMITTER/RECEIVER needs service | Unused
YY | Status Report | This is a header for an account status report transmission | Unused
YZ | Service Completed | Required TRANSMITTER / RECEIVER service completed | Mfr defined
ZA | Freeze Alarm | Low temperature detected at premises | Zone or point
ZB | Freeze Bypass | Low temperature detection has been bypassed | Zone or point
ZH | Freeze Alarm Restore | Alarm condition eliminated | Zone or point
ZJ | Freeze Trouble Restore | Trouble condition eliminated | Zone or point
ZR | Freeze Restoral | Alarm/trouble condition has been eliminated | Zone or point
ZS | Freeze Supervisory | Unsafe freeze detection system condition | Zone or point
ZT | Freeze Trouble | Zone disabled by fault | Zone or point
ZU | Freeze Unbypass | Low temperature detection bypass removed | Zone or point

## TLINK 150-250
Description/Event | Automation Message | TLINK
Panel Absent | ET0001 | TL-250
Panel Restored | ER0001 | TL-250
FTC1 Alarm | YC0001 | TL-250
FTC1 Restoral | YK0001 | TL-250
FTC2 Alarm | YC0002 | TL-250
FTC2 Restoral | YK0002 | TL-250
PC5108 Tamper Alarm | ES0000 | TL-250
PC5108 Tamper Restoral | EJ0000 | TL-250
PC5108 Absent | ET0002 | TL-250
PC5108 Restored | ER0002 | TL-250
Keyswitch Arm | CS0000 | TL-250
Keyswitch Disarm | OS0000 | TL-250
Remote Programming Start | RB0000 | TL-250
Remote Programming End | RS0000 | TL-250
Local Programming Start | LB0000 | TL-250
Local Programming End | LS0000 | TL-250
Internal Comm. Error | YC0000 | TL-250
Zone Alarms | UA-XXX | TL-150
Zone Alarm Restorals | UH-XXX | TL-150
[F] Alarm | FA-000 | TL-150
[A] Alarm | MA-000 | TL-150
[P] Alarm | PA-000 | TL-150
[F] Alarm Restoral | FH-000 | TL-150
[A] Alarm Restoral | MH-000 | TL-150
[P] Alarm Restoral | PH-000 | TL-150
2-wire Smoke Alarm | FA-000 | TL-150
2-wire Smoke Alarm Restoral | FH-000 | TL-150
AC Trouble | AT-000 | TL-150
AC Trouble Restore | AR-000 | TL-150
Duress Alarm | HA-000 | TL-150
Fire Trouble Alarm | FT-000 | TL-150
Fire Trouble Alarm Restoral | FJ-000 | TL-150
Low Battery Trouble | YT-000 | TL-150
Low Battery Trouble Restore | YR-000 | TL-150
Bell Circuit Trouble | YH-000 | TL-150
Bell Circuit Trouble Restore | YA-000 | TL-150
General Supervisory Trouble | ET-000 | TL-150
General Supervisory Trouble Restore | ER-000 | TL-150
General System Trouble | YX-000 | TL-150
General System Trouble Restore | YZ-000 | TL-150
Opening After Alarm | OR-000 | TL-150
Partial Closing | CF-000 | TL-150
TLM Trouble (line number) | LT-XXX | TL-150
TLM Trouble Restore (line number) | LR-XXX | TL-150
Periodic Test | RP-000 | TL-150
Periodic Test with Trouble | RY-000 | TL-150
Recent Closing | CR-000 | TL-150
Expansion Module Supervisory Trouble | UA-000 | TL-150
Expansion Module Supervisory Restore | UH-000 | TL-150
Zone Tampers | TA-XXX | TL-150
Zone Tamper Restorals | TR-XXX | TL-150
Zone Troubles | UT-XXX | TL-150
Zone Trouble Restorals | UJ-XXX | TL-150
General System Tamper | ES-000 | TL-150
General System Tamper Restoral | EJ-000 | TL-150
FTC Restoral | YK-000 | TL-150